## Zone 1
General Data | 1.0 | Customer Data
| 1.1 | Data Sheet No.
| 1.2 | Location: | ASHKELON
| 1.3 | Plant/Unit: | ASHKELON
| 1.4 | Project Name:
| 1.6 | Transformer Tag Number | TRG1, TRG2
| 1.7 | Max./Min. Ambient. Temp.: | 0-450C
| 1.8 | Altitude Over Sea Level | less than 10m
| 1.9 | Relative Humidity: | 95%
| 1.10 | Atmosphere: | Petrochemicals
| 1.14 | Specification:
| 1.15 | Prepared By: | A.NAHARI
| 1.16 | Date: | 2024-01-28
Transformer Data | 2.0 | Customer Transformer Data
| 2.1 | Transformer Type | Oil Imerased Sealed
| 2.2 | Rated Power | 2500 | KVA
| 2.3 | Rated Secondary Voltage | 400 | V
| 2.4 | Rated Primary Voltage | 6600 | V
| 2.5 | Frequency: | 50 | Hz
| 2.6 | Tap Changer Steps | ±2x2.5 | %
| 2.7 | Connection (Vector) Group | YnD-11
| 2.8 | Suitable for outdoor installation | Yes
| 2.9 | Primary Connecting Cable Size/Secondary Connection | 3(1X95) N2XSY | mm2
| 2.10 | Primary Terminal's Rated Current | 630 | A
General Data | 3.0 | Manufacturer transformer Data
| 3.1 | Prepared By:
| 3.2 | Date:
| 3.3 | Manufacturer:
| 3.4 | Transformer Type
| 3.5 | Type of cooling
Electrical Data | 3.5 | Rated Power |  | KVA
| 3.6 | Short-circuit impedance at rated current at 750C, Xk |  | %
| 3.7 | Temperature rise of the top layer of oil: |  | 0C
| 3.8 | Temperature rise of the windings: |  | 0C
| 3.9 | Rated short circuit current for 2 sec. |  | (KA)
| 3.10 | No-load current: |  | %xIn
| 3.11 | No-load losses: |  | W
| 3.12 | Rated load losses at 750C |  | W
| 3.13 | Noise level (measured at a distance of one meter): |  | db (A)
| 3.14 | Total Weight |  | Kg.
| 3.15 | Weight of Oil |  | Kg.
| 3.16 | Dimensions [W x L x H] |  | cm.
| 3.17 | Type of mineral oil
High Voltage | 3.18 | High voltage winding material:
| 3.19 | High Voltage bushings type and manufacturer (PLUGS INCLUDED)
| 3.20 | Number of high voltage bushings:
| 3.21 | Rated voltage of the high voltage bushings: |  | KV
| 3.22 | Creepage distance of the high voltage bushing: |  | mm.
| 3.23 | Rated current of the high voltage bushing: |  | A
| 3.24 | Rated lightning impulse withstand voltage 1.2/50 msec. |  | KV peak
| 3.25 | Rated short duration power frequency withstand voltage at 50Hz, 1min. |  | KV r.m.s
Low Voltage | 3.26 | Low voltage winding material:
| 3.27 | Low Voltage bushings type and manufacturer
| 3.28 | Number of low voltage bushings:
| 3.29 | Rated voltage of the low voltage bushings: |  | KV
| 3.30 | Creepage distance of the low voltage bushing: |  | mm.
| 3.31 | Rated current of the low voltage bushing: |  | A