## גיליון1
Data sheet for: |  | ULTRASONIC FLWMETER FLOWMETER 6" 150# bidirectional |  |  |  | Tag No. | : 000-FT-
GENERAL |  | SERVICE | DESTILATES
|  | FLOWMETER TYPE | ULTRASONIC
|  | AREA CLASSIFICATION | ZONE 2 GROUP A
|  | LINE NUMBER / SIZE | 6" 150#
|  | APPLICATION | INVENTORY CONTROL & LEAK DETECTION
PROCESS DATA |  | PROCESS FLUID | OIL DISTILLATE WITH UP TO 15% MTBE
|  | FLOW: MAX / MIN. / OPER. | 600 m3/h |  |  | 100 m3/h | 450 m3/h
|  | PRESS. MAX / PRESS. OPER. | 19 bar
|  | TEMP. MAX / TEMP. OPER. | 60 °C |  |  |  | AMB.
|  | OPER. DENSITY | 0.70-0.86
|  | SOLIDS / BUBBLES | < 5% VOL. |  |  |  | < 1% VOL.
|  | FLOW | BIDIRECTIONAL
METERING |  | LINEARITY | < ± 0.15% of measured value (under reference conditions)
|  | REPETABILITY | < ±0.02%
|  | UNCERTAINTY | < ± 0.027% conforms to API standard
|  | ZERO stability | < 1 mm/s
|  | ACCUARICY/CERTIFICATION | CLASS 0.3 OIML R117-1 CUSTODY TRANSFER
|  | LINEARITY | ±0.15%
TRANSMITTER |  | TYPE | ALTSONIC 5
|  | POWER SUPPLY | 24 VDC
|  | ENCLOSURE | IP 67
|  | PROTECTION | Eex ib IIA
|  | CALIBRATION | 6 POINT 3 REPEATS
|  | FREQUENCY OUTPUT SIGNAL | 2
|  | ANALOG OUTPUT (4-20 mA) | DENSITY-PROGRAMED
|  | COMUNICATION PORT | YES | (SEE NOTES)
|  | MOUNTING / PAINTING | FIELD |  |  |  | BY VENDOR
|  | ELECTRICAL CONNECTION | YES
|  | LOCAL DISPLAY | LOCAL FULL PROGAMABLE OPTION
|  | CALIBRATION | YES
|  | CERTIFICATION | YES
|  | FLOW CONDITIONER | YES X2
NOTES |  | THE METER WILL BE PROVIDED WITH COMUNICATION SOFWARE& LICENCE
MANUFACTURE |  | KROHNE ONLY
RS232/485 MODBUS RTU OUTPUT
תשתיות נפט ואנרגיה בע"מ
[6 empty] | DATA SHEET : FT05 | PAGE 1 OF 1
REV. | DATE | DESCRIPTION | BY | CHK | APP | REF P&ID: | PROJECT No.