## גיליון1
July 10, 2024 Ref.: 314566 To: All Tender Participants Dear Sir / Madam, Re: Public Tender No. PD24000987 (the “Tender”) – Clarification The Company has received certain requests for clarification regarding the Tender, in accordance with Section 5.1 thereof, provided below (the “Questions”). Next to each Question is the Company’s answer, which shall be considered by the Company as authoritative.
NO | ISSUE TYPE | Question |  |  |  | Answer
1 | Technical | sadly a 10'' unit would not be suitable for a flow of 200 GPM / 454M3/HR can the flow be capped? This would need to be capped at 330 M3/HR to use a 10'' lined product. If not, the only product that could be offered be a 14'' DUPLEX (see attached GA for reference) |  |  |  | Not accepted
2 | Technical | FILTER FLOW RATE: technical proposal for required service is model 11M-314, suitable for a maximum flow rate of 2200 usgpm when equipped with EI-1590 qualified 5 microns filter elements |  |  |  | FILER ELEMENT ACCORDING TO SPEC.
3 | Technical | Vessel rating flange connections: ANSI 150# RF flanges - |  |  |  | PLS' QUOTE YOR SUGGETION FOR DRAIN CONNECTION
flange rating for inlet and outlet connections only. There is no provision for drain flanged connection.
4 | Technical | Design pressure: 10.3 bar @ 121 °C - |  |  |  | ACCEPTED
Because of filter element maximum temperature of 115 °C (240 °F), we ask to limit design temperature to 115 °C. This limitation does not affect pressure vessel mechanical design but will prevent operating issues due to cartridge failure.
5 | Technical | The exterior surface shall be epoxy painted according to manufacturer standard. coating External consists of 50micron primer. Customer needs to confirm acceptance and compliance or provide further details about required external coating cycle. |  |  |  | ACCORDING TO SPEC. EPOXY COATING
6 | Technical | The vessels shall be stamped and certified to ASME Code Section VIII. |  |  |  | ACCEPTED
Pressure vessels will be designed and calculated according to ASME Code Section VIII, Division 1, but without ASME Stamp EMEA pressure vessels follow PED directive 2014/68/EU. Ask for a deviation.
7 | Technical | Each filter shall be fitted with the following accessories: |  |  |  | ACCEPTED
1" Diameter Bottom Drain valve & plug drain.
Vessel bottom drain and inlet drain connections size are diameter 3/4”.
ask for a deviation
8 | Technical | 3/4" Steel, NPT, Automatic air vent fitted with check valve manufacture by "Gammon" models GTP-11 & GTP-2916. |  |  |  | ACCEPTED
Armstrong standard 11-AV instead of Gammon (see attached bulletin).
Ask for a deviation.
9 | Technical | 3/4", Aluminum, NPT, Pressure relief valve, pressure set point according to vessel pressure rating. |  |  |  | ACCEPTED
Use standard TRV in AISI 316 (see attached bulletin).
Ask for a deviation
10 | Technical | 1/4" NPT, Differential Pressure gauging unit manufacture by "Gammon", model GTP- 534, Aluminum construction. The unit shall be fitted with 3-way test valve, a built-in thermal relief valve and peak hold. |  |  |  | WE ASK FOR GEMMON DP
Use standard Schultz gauges instead of Gammon (see attached bulletin).
Ask for a deviation.
11 | Technical | The vessels elements cartridges shall be hold in position against vibration by a spider assembly |  |  |  | ACCEPTED
Ask to confirm (designed as per our standard
12 | Technical | 1" NPT vessel side entry. |  |  |  | ACCEPTED
Vessel side entry - vessel slow filling operation - is diameter 3/4".
Ask for a deviation.
13 | Technical | Section “Nozzles Connections Descriptions” at page 4 of 5 |  |  |  | NOT ACCEPTED
|  | Nozzles | Flange / BSP | Size | Rating
|  | Inlet | RF | 8" | 150#
|  | Outlet | RF | 8" | 150#
|  | Main Drain | BSP | 3/4” | 3000#
|  | Vent | BSP | 3/4” | 3000#
|  | Pressure Relief | BSP | 3/4” | 3000#
|  | Inlet Nozzle Drain | BSP | 3/4" | 3000#
|  | Differential Pressure | BSP | 1/4" | 3000#
|  | Sampling | BSP | 1/2" | 3000#
|  | Slow Filling | BSP | 3/4” | 3000#
Clarifications and request for deviations marked in red.
14 | Technical | Section “Commercials Terms” at page 5 of 5 |  |  |  | ACCEPTED
In order to evaluate the tender’s quotation, the following information must be given:
Unit drawings.
Operation and maintenance instruction.
Accessories drawings.
List of recommended spare parts with pricing.
Delivery date.
List of Israeli customers including contact address.
Price for the offer.
Technical documents attached to this communication.
Further details shall be provided with the commercial quotation and supplied in case of order.
15 | Technical | Section “Guarantee” at page 5 of 5 |  |  |  | ACCEPTED
The vender shall guarantee materials and workmanship for a period of 12 months from the date of commissioning.
Should any defect due to faulty design, materials or bad workmanship become apparent during the guarantee period, the vendor shall repair or otherwise rectify the defects, and free of charge to purchaser. Changes shall be made at a time and in a manner agreeable to the client.
The equipment is guaranteed against faulty design, materials, and workmanship for 12 months from date of commissioning or 18 months from date of dispatch, whichever is earlier.
Ask for a deviation
Thank you for your continued interest in the Tender; we look forward to receiving your bids. Sincerely, Eran Rheinisch Procurement and Engagements Department